## COVER
THERMAX LIMITED
WATER & WASTE SOULTIONS
PUNE — 411 026
TITLE
CLIENT
CONSULTANT
PROJECT
THERMAX O.C. NO.
THERMAX DOC. NO. / CLIENT DOC. NO.
| REV NO. | DATE | DESCRIPTION | PREPD BY | CHKD BY | APPD. BY | 5.5

## INSTRUCTION TO VENDOR
OC NO- INSTRUCTIONS TO LT MOTOR VENDORS
A) | OFFER :
Vendor shall give offer for motors based on following documents enclosed:-
| Sr. No. | Item Description |  |  |  | Document Number |  |  |  |  | Pages
1
2
3
4
[9 empty] | Total Pages |  | 0
The offer shall be strictly based on the document mentioned above. Deviations if any shall be
clearly highlighted in the offer in the deviations format enclosed, otherwise it is presumed that
there is no deviation. Vendor shall obtain the necessary clarity from Thermax regarding the
discrepancy if any in the specifications furnished. Technical literature shall be furnished
along with the offer. Vendor shall enclose along with his offer the purchase specifications of
Thermax stamped as "Accepted ". Offer not in line with the above shall be summarily rejected.
Offer complete in all respects should be received by us within 6 days from the date of this enquiry.
B) | DRAWING SUBMISSION :
Following documents shall be submitted to us for our / our client’s approval in ' 1 ' sets.
However drawing submission, approval, inspection and / or certification does neither relieve the
vendor of his responsibility for furnishing the equipment confirming to the requirement of purchase
specification nor prejudice any claim.
|  | Along with the offer |  |  | After placement of order | [5 empty] | Time
| 1. Signed & stamped inquiry |  |  | 1. Motor data sheet ,
| document |  |  | Motor & terminal box GA drawings
| 2. Motor data sheet, Motor GA, |  |  | 2. Characteristic Curves
| TB GA etc. |  |  |  | a) torque vs speed | [5 empty] | 3 days
| 3. Deviation list ( if any ) |  |  |  | b) current vs speed
| 4. List of spares provided as per |  |  |  | c) current vs time
| specs (if any) |  |  |  | d) thermal withstand ( hot & cold )
| 5. QAP |  |  | 3. Any other doc./drg. as mentioned in
| 6. Technical Literature |  |  | specs enclosed/required by our clients.
Vendor shall refer motor list for final cable size. Vendor shall provide terminal
box, TB & cable entry suitable for final cable sizes indicated by us. The drawings submitted shall be
legible and correct as per specification & shall not call for resubmission.
C) | FINAL DOCUMENTATION :
Vendor shall submit '01' sets of O&M manuals to our office.
D) | IMPORTANT NOTES:
1) | Motors shall be suitable for "torque v/s speed" characteristics of driven equipt which shall be furnished
later.
2) | If load GD2 value is not furnished, load GD2 may be considered equal to motor GD2.
3) | To select motor rating, consider pumps discharge valve in open condition
4) | To select motor rating, consider blowers damper in open condition
5) | Motor Data-sheets, curves & Drawings shall be submitted in a single PDF file.
6) | Vendor shall select the appropriate motor (frame size, bearings etc.) based on type of motor starter
(DOL/VFD/Star-delta/Soft starter), type of coupling & driven equipment/application.
7) Vendor to submit this document duly signed & stamped for our records.
8) Any deviation on this Motor Specifications Vendor has to convey the same at Bid Stage only.
During detail Engineering any deviation shall not be entertained.
11) Main Terminal Box Add On Cost for Higher size TB shall be given with the Offer. Maximum Cable Size
for the Terminal Box shall be confirmed during Bid stage only.
Thermax Ltd. |  |  | Clients : |  |  |  | Rev. | Date |  | Prepd. |  | Chkd. |  | Appd.
Water & Waste Solutions |  |  | Consultants : |  |  |  | Spec. No. | [5 empty] | Sh. No.
Pune - 411 026 |  |  | O.C. No. : | [10 empty] | of

## MOTOR SPECIFICATION
Sr. No. | Description | Specification
A | DESIGN PARAMETER
1 | Ambient Temperature | 50 Deg. C
2 | Altitude
3 | Area Classification | Safe | yes generate Separate Documuent for Safe & hazardous motors
4 | Voltage | 415, ± 10%
5 | Frequency | 50 Hz ± 5%
6 | Combined Voltage & Frequency Variation | ± 10%
B | ELECTRICAL PARAMETER
1 | Applicable Standards | - IEC-60034 / IS 12615 (latest revision) | Not requried drop down
2 | Type | Low Voltage Squirrel Cage Induction Motor | Not requried drop down
3 | Duty | S1 | cell should be editable
4 | Service Factor | 1 | cell should be editable
5 | Motor Ratings | As per Motor List
6 | No. of Pole requirement | As per Motor List
7 | Type of Starting Method | As per Motor List
8 | Type of Mounting | As per Motor List
9 | Degree of Protection | IP - 55 / IP-56 / IP-65 | BY DEFAULT IP55 VALUE
10 | Insulation Class | "F"
11 | Temp. rise limited to | Limited to class 'B'
12 | Efficiency Class | As per Motor List
13 | Type of Cooling | TEFC | cell should be editable
14 | Starting current | Shall be as per IS 12615
15 | TB Fault KA | 50 KA for 0.25 Sec. for motors
C | MECHANICAL PARAMETER
1 | Frame Material | Cast Iron/Al. | DROP DOWN
2 | Material of Terminal Box | Cast Iron/Al. | DROP DOWN
3 | Terminal Box Location | At Top (The terminal box shall be capable of being turned through 360 deg in steps of 90 deg) | cell should be editable & BY DEFAULT VALUE IS TOP MOUNTED
4 | Vibration Level | Shall be limited as per IS 12075-1986
5 | Noise Level | As per IS: 12065-1987/IEC690034-14
6 | Paint Type & Shade | USER DEFINED | cell should be editable
D | GENEARL PARAMETER
1 | Starts / Hour permissibe | 2 Hot and 3 Cold (DEFAULT VALUE) | cell should be editable
2 | Direction of Roration | Bidirection
3 | Space Heater | As per Motor List
4 | Thermistor | As per Motor List
5 | RTD/BTD | As per Motor List
6 | Motor connections | As per Motor Manufacturing Standard
7 | Power Cable to Motor | As per Motor List
8 | Bearing | As per Motor List
9 | Earthing | Motor Body & TB Earthing Terminal To be provided.
Note on C3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on B5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: We believe orange color cells needs to be in UI and should have dropdown values
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drop down & write access
Note on C18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on C20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is a default value. It will change as per project requirement
Note on B24: Abhinandan Ashok Chougule: to be populated from design parameter
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drop down , write access & as per OEM

## MOTOR LIST
630390- LT MOTOR LIST-R0
SR.NO. | TAG. NO. | DESCRIPTION | WORKING/STANDBY | MOTOR RATING (KW) | RPM | TYPE OF MOUNTING | MOTOR FRAME SIZE | MOTOR GD2 (kgf.m2) | GD2 of Driven Equipment | Bkw | TYPE OF COUPLING | LOCATION | VOLTAGE (VOLT) | FREQUENCY (Hz) | FEEDER TYPE | CABLE SIZE | SPACE HEATER | ROLLER BEARING | INSULATED BEARING | THERMISTOR | RTD / BTD | MOTOR ENERGY EFFICIENCY | FULL LOAD CURRENT | POWER FACTOR | MOTOR EFFICIENCY AT 100% | MAKE | PARTCODE | REMARK
1 | K-101A | SUF Air Blower-A | W | 18.5 | 1500 | B3 | LATER | LATER | LATER | 14.12 | V-BELT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 10 SQ.MM. CU. XLPE ARMOURED CABLE | NO | YES | NO | NO | NO | IE3 |  |  |  | CG |  | 0
2 | K-101B | SUF Air Blower-B | S | 18.5 | 1500 | B3 | LATER | LATER | LATER | 14.12 | V-BELT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 10 SQ.MM. CU. XLPE ARMOURED CABLE | NO | YES | NO | NO | NO | IE3 | [5 empty] | 0
3 | 120-P-102A | SUF Permeate Pump-A | W | 5.5 | 1500 | B3 | LATER | LATER | LATER | 19.17 | DIRECT | OUTDOOR | 415 | 50 | VFD | 1R X 3.5C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | YES | YES | NO | IE3 | [5 empty] | 0
4 | 120-P-102B | SUF Permeate Pump-B | W | 5.5 | 1500 | B3 | LATER | LATER | LATER | 19.17 | DIRECT | OUTDOOR | 415 | 50 | VFD | 1R X 3.5C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | YES | YES | NO | IE3 | [5 empty] | 0
5 | 120-P-102C | SUF Permeate Pump-C | S | 5.5 | 1500 | B3 | LATER | LATER | LATER | 19.17 | DIRECT | OUTDOOR | 415 | 50 | VFD | 1R X 3.5C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | YES | YES | NO | IE3 | [5 empty] | 0
6 | 120-P-104A | Filter Feed Pump-A | W | 5.5 | 1500 | B3 | LATER | LATER | LATER | 19.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
7 | 120-P-104B | Filter Feed Pump-B | S | 5.5 | 1500 | B3 | LATER | LATER | LATER | 19.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
8 | 120-P-104C | Filter Feed Pump-C |  |  | 1500 | B3 | LATER | LATER | LATER | 19.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 25 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
9 | 120-W-103A | Filter Backwash Pump-A |  |  | 3000 | B3 | LATER | LATER | LATER | 8.14 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 6 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
10 | 120-W-103B | Filter Backwash Pump-B |  |  | 3000 | B3 | LATER | LATER | LATER | 8.14 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 6 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
11 | 120-P-103A | SUF CIP/ Backwash Pump-A |  |  | 1500 | B3 | LATER | LATER | LATER | 18.53 | DIRECT | OUTDOOR | 415 | 50 | VFD | 1R X 3.5C X 16 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | YES | YES | NO | IE3 | [5 empty] | 0
12 | 120-P-103B | SUF CIP/ Backwash Pump-B |  |  | 1500 | B3 | LATER | LATER | LATER | 18.53 | DIRECT | OUTDOOR | 415 | 50 | VFD | 1R X 3.5C X 16 SQ.MM. AL. XLPE ARMOURED CABLE | NO | NO | YES | YES | NO | IE3 | [5 empty] | 0
13 | 120-P-105A | Treated Water Transfer pump-A |  |  | 3000 | B3 | LATER | LATER | LATER | 65.46 | DIRECT | OUTDOOR | 415 | 50 | DOL | 2R X 3C X 50 SQ.MM. AL. XLPE ARMOURED CABLE | YES | NO | NO | NO | NO | IE3 | [5 empty] | 0
14 | 120-P-105B | Treated Water Transfer pump-B |  |  | 3000 | B3 | LATER | LATER | LATER | 65.46 | DIRECT | OUTDOOR | 415 | 50 | DOL | 2R X 3C X 50 SQ.MM. AL. XLPE ARMOURED CABLE | YES | NO | NO | NO | NO | IE3 | [5 empty] | 0
15 | 120-P-105C | Treated Water Transfer pump-C |  |  | 3000 | B3 | LATER | LATER | LATER | 65.46 | DIRECT | OUTDOOR | 415 | 50 | DOL | 2R X 3C X 50 SQ.MM. AL. XLPE ARMOURED CABLE | YES | NO | NO | NO | NO | IE3 | [5 empty] | 0
16 | 120-P-107A | HRSCC Feed Pump-A |  |  | 1500 | B3 | LATER | LATER | LATER | 3.36 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
17 | 120-P-107B | HRSCC Feed Pump-B |  |  | 1500 | B3 | LATER | LATER | LATER | 3.36 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
18 | 120-P-108A | Filter Press Feed Pump-A |  |  | 1500 | B35 | LATER | LATER | 0.008963 | 1.59 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
19 | 120-P-108B | Filter Press Feed Pump-B |  |  | 1500 | B35 | LATER | LATER | 0.008963 | 1.59 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
20 | P-204A | Sodium Hypo Chlorite dosing Pumps-A |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
21 | P-204B | Sodium Hypo Chlorite dosing Pumps-B |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
22 | P-206A | NaoH dosing Pumps-A |  |  | 1500 | B3 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
23 | P-206B | NaoH dosing Pumps-B |  |  | 1500 | B3 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
24 | P-205A | Acid dosing Pumps-A |  |  | 1500 | B3 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
25 | P-205B | Acid dosing Pumps-B |  |  | 1500 | B3 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
26 | P-202A | PE dosing pump-A |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
27 | P-202B | PE dosing pump-B |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
28 | P-203A | DWPE dosing pump-A |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
29 | P-203B | DWPE dosing pump-B |  |  | 1500 | B5 | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
30 | A-101 | Flash mixer |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
31 | A-103A | Agitator for Alum dosing tank-A |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.16 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
32 | A-103B | Agitator for Alum dosing tank-b |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.16 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
33 | A-104A | Agitator for PE dosing tank-A |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.2 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
34 | A-104B | Agitator for PE dosing tank-B |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.2 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
35 | A-105A | Agitator for DWPE dosing tank-A |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
36 | A-105B | Agitator for DWPE dosing tank-B |  |  | 1500 | B5 | LATER | LATER | 0.004 | 0.31 | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
37 | A-109 | Agitator for NaoH dosing Tank |  |  | LATER | LATER | LATER | LATER | LATER | LATER | DIRECT | OUTDOOR | 415 | 50 | DOL | 1R X 3C X 2.5 SQ.MM. CU. XLPE ARMOURED CABLE | NO | NO | NO | NO | NO | IE3 | [5 empty] | 0
[19 empty] | R0 | 18.08.2023 | ISSUED FOR QUOTATION |  |  |  |  | SDP | TTS | VSJ
[19 empty] | REV. NO. | DATE | ISSUED FOR |  |  |  |  | PREPARED BY | CHECKED BY | APPROVED BY
Note on E2: Abhinandan Ashok Chougule:
Note on N2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Input from main UI
Note on O2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Input from main UI
Note on Q2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: from cable sizing calculation
Note on AA2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: COLUMN NOT FOR WWS-IPG
Note on AB2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: COLUMN FOR WWS & Enviro standard part code list will be shared

## MOTOR BOM
LT MOTOR BOM
Sr.No. | PARTCODE | Description | Unit | Qty | Remark
1 |  | CG MAKE LT MOTOR : 0.37 KW, 4 POLE, V1 MOUNTED, IE3 | NOS | 3
2 |  | CG MAKE LT MOTOR : 0.37 KW, 6 POLE, V1 MOUNTED, IE3 | NOS | 0
3 |  | CG MAKE LT MOTOR : 0.37 KW, 4 POLE, B5 MOUNTED, IE3 | NOS | 13
4 |  | CG MAKE LT MOTOR : 0.37 KW, 4 POLE, B3 MOUNTED, IE3 | NOS | 0
DO NOT UPLOAD
NOTE : FOR WWS - IPG, MAKE OF MOTOR NOT TO BE DISPLAYED IN BOM & PARTCODE COLUMN WILL BE BLANK FOR FOR IPG.

## VOID (hidden)
92013-COMBINE LIST-R0
| DESCRIPTION | TAG. NO. | QUANTITY (NOS.) | FEED FROM | WORKING / STANDBY | MOTOR RATING (KW) |  | RPM | LOAD FACTOR | TYPE OF MOUNTING | MOTOR FRAME SIZE | MOTOR RPM | MOTOR GD2 | GD2 of Driven Equipment | Bkw | TYPE OF COUPLING | LOCATION | PHASE | VOLTAGE (VOLT) | FREQUENCY (Hz) | FEEDER TYPE | SPEED VARIATION | FEEDER SCHEME | WORKING LOAD | STANDBY LOAD | CABLE SIZE | LPBS | SPACE HEATER | THERMISTOR | RTD | ROLLER BEARING | INSULATED BEARING | REMARK | MOTOR ENCLOSURE PROTECTION | MOTOR ENERGY EFFICIENCY | MOTOR SCOPE | FEED FROM | PANEL SCOPE
2 | Raw water Sludge transfer pump-A | P-101A | 1 | MCC | W | 3.7 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 78.53 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
2 | Raw water Sludge transfer pump-B | P-101B | 1 | MCC | S | 3.7 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 78.53 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
1 | Raw water feed pump-A | P-102A | 1 | MCC | W | 18.5 | 18.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 78.53 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 18.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
1 | Raw water feed pumps-B | P-102B | 1 | MCC | S | 18.5 | 18.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 78.53 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 18.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
3 | HRSCC Drain / Sludge transfer pump-A | P-126A | 1 | MCC | W | 3.7 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.34 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
3 | HRSCC Drain / Sludge transfer pump-B | P-126B | 1 | MCC | S | 3.7 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.34 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
4 | Filter feed pumps-A | P-103A | 1 | MCC | W | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.34 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 11 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
4 | Filter feed pumps-B | P-103B | 1 | MCC | W | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.34 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 11 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
4 | Filter feed pumps-C | P-103C | 1 | MCC | S | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.34 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 11 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
5 | Filter Back wash pump-A | P-104A | 1 | MCC | W | 15 | 15 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 41.35 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 15 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
5 | Filter Back wash pump-B | P-104B | 1 | MCC | S | 15 | 15 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 41.35 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 15 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
6 | Softener Feed Pump-A | P-105A | 1 | MCC | W | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 41.35 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 11 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
6 | Softener Feed Pump-B | P-105B | 1 | MCC | W | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 41.35 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 11 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
6 | Softener Feed Pump-C | P-105C | 1 | MCC | S | 11 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 41.35 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 11 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
7 | Regeneration Waste Transfer Pump-A | P-121A | 1 | MCC | W | 5.5 | 7.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 11.2 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 5.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
7 | Regeneration Waste Transfer Pump-B | P-121B | 1 | MCC | S | 5.5 | 7.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 11.2 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 5.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
8 | Make up Water Transfer Pump-A | P-106A | 1 | MCC | W | 30 | 30 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 11.2 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 30 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
8 | Make up Water Transfer Pump-B | P-106B | 1 | MCC | S | 30 | 30 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 11.2 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 30 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
9 | Potable Water Transfer Pump-A | P-107A | 1 | MCC | W | 5.5 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 5.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
9 | Potable Water Transfer Pump-B | P-107B | 1 | MCC | S | 5.5 | 5.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 5.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
10 | DMF Air blowers-A | K-101A | 1 | MCC | W | 7.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 7.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
10 | DMF Air blowers-B | K-101B | 1 | MCC | S | 7.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 7.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
11 | NaoCl dosing pump-A | P-201A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
11 | NaoCl dosing pump-B | P-201B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 20.78 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
12 | FeCl3 dosing pump-A | P-202A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
12 | FeCl3 dosing pump-B | P-202B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
13 | PE dosing pump-A for HRSCC | P-203A | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
13 | PE dosing pump-B for HRSCC | P-203B | 1 | MCC | S | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
14 | SMBS dosing pump-A | P-204A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | 10-100% | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
14 | SMBS dosing pump-B | P-204B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 33.55 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | 10-100% | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
15 | Flash mixer | A-101 | 1 | MCC | W | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 30.64 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
16 | Common Brine tank mixer | A-102 | 1 | MCC | W | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 30.64 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
21 | HRSCC - Turbine drive with VFD | HM-101 | 1 | MCC | S | 2.2 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 4.18 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 2.2 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
20 | HRSCC mechanism - Scrapper | HM-102 | 1 | MCC | W | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 4.18 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
23 | CT Fan | E-103A | 1 | MCC | W | 75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.41 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
23 | CT Fan | E-103B | 1 | MCC | W | 75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.41 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
23 | CT Fan | E-103C | 1 | MCC | S | 75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.41 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
24 | Supply Pump-A to RHF & Ind. Heater welding machine | P-108A | 1 | MCC | W | 250 | 260 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.23 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 250 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
24 | Supply Pump-B to RHF & Ind. Heater welding machine | P-108B | 1 | MCC | S | 250 | 260 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.23 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 250 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
26 | Supply Pump-A to Rolling Mill | P-111A | 1 | MCC | W | 200 | 160 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 22.69 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 200 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
26 | Supply Pump-B to Rolling Mill | P-111B | 1 | MCC | W | 200 | 160 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 22.69 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 200 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
27 | Supply Pump-A to Air compressor | P-110A | 1 | MCC | W | 160 | 150 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 22.69 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 160 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
27 | Supply Pump-B to Air compressor | P-110B | 1 | MCC | S | 160 | 150 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 22.69 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 160 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
28 | SUPPLY PUMS TO SIDE STREAM FILTER CUM BACKWASH PUMP-A | P-112A | 1 | MCC | W | 75 | 55 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 73.26 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
28 | SUPPLY PUMS TO SIDE STREAM FILTER CUM BACKWASH PUMP-B | P-112B | 1 | MCC | S | 75 | 55 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 73.26 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
29 | SSF Air blower-A | K-102A | 1 | MCC | W | 9.3 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 73.26 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 9.3 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
29 | SSF Air blower-B | K-102B | 1 | MCC | S | 9.3 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 73.26 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 9.3 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
30 | Scale & Corrosion Inhibitor dosing pump-1 | P-205A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.6 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
30 | Scale & Corrosion Inhibitor dosing pump-1 | P-205B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.6 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
31 | Polymeric Dispersant dosing pump-1 | P-206A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.6 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
31 | Polymeric Dispersant dosing pump-1 | P-206B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.6 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
32 | Acid dosing pump-A | P-207A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.3 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC | LOCAL VFD
32 | Acid dosing pump-B | P-207B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.3 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC | LOCAL VFD
34 | Biocide dosing pump-II-A | P-209A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.55 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
34 | Biocide dosing pump-II-B | P-209B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.55 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
38 | CT Fan for Filtered cold water well | E-104A | 1 | MCC | W | 90 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 90 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
38 | CT Fan for Filtered cold water well | E-104B | 1 | MCC | W | 90 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 90 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
38 | CT Fan for Filtered cold water well | E-104C | 1 | MCC | W | 90 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 90 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
38 | CT Fan for Filtered cold water well | E-104D | 1 | MCC | S | 90 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 90 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
39 | Supply pump-A to Mill direct cooling | P-113A | 1 | MCC | W | 315 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 315 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
39 | Supply pump-B to Mill direct cooling | P-113B | 1 | MCC | W | 315 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 315 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
39 | Supply pump-C to Mill direct cooling | P-113C | 1 | MCC | W | 315 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 315 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
39 | Supply pump-D to Mill direct cooling | P-113D | 1 | MCC | S | 315 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.15 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 315 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
40 | Supply Pump-A to Thermo Processing Line | P-114A | 1 | MCC | W | 655 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 655 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
40 | Supply Pump-B to Thermo Processing Line | P-114B | 1 | MCC | W | 655 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 655 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
40 | Supply Pump-C to Thermo Processing Line | P-114C | 1 | MCC | W | 655 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 655 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
40 | Supply Pump-D to Thermo Processing Line | P-114D | 1 | MCC | S | 655 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 655 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
47 | HRF Backwash Pump-A | P-115A | 1 | MCC | W | 37 | 30 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.507 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
47 | HRF Backwash Pump-B | P-115B | 1 | MCC | S | 37 | 30 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.507 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
44 | Fire hydrant Jockey Pump | P-116A | 1 | MCC | W | 15 | 75 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.32 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 15 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
45 | Fire hydrant Main Pump | P-116B | 1 | MCC | W | 75 | 11 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.234 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-A | P-117A | 1 | MCC | W | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 225 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-B | P-117B | 1 | MCC | W | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 225 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-C | P-117C | 1 | MCC | W | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 225 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-D | P-117D | 1 | MCC | W | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 225 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-E | P-117E | 1 | MCC | W | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 225 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
42 | Contaminated Hot Water pumps to HRF-F | P-117F | 1 | MCC | S | 225 | 200 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | 10-100% | VFD-1 | 0 | 225 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
46 | Oil Transfer pump-A | P-118A | 1 | MCC | W | 2.2 | 1.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.234 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 2.2 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
46 | Oil Transfer pump-B | P-118B | 1 | MCC | S | 2.2 | 1.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.234 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 0 | 2.2 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
55 | HRF Air blower-A | K-103A | 1 | MCC | W | 75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
55 | HRF Air blower-B | K-103B | 1 | MCC | W | 75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
48 | Backwash Sump pump-A to Thickener | P-122A | 1 | MCC | W | 55 | 37 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.507 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 55 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
48 | Backwash Sump pump-B to Thickener | P-122B | 1 | MCC | S | 55 | 37 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.507 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 0 | 55 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
49 | Thickener underflow pump-A | P-123A | 1 | MCC | W | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
49 | Thickener underflow pump-B | P-123B | 1 | MCC | S | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-2 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
50 | Belt press feed pump-A | P-125A | 1 | MCC | W | 30 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 30 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
50 | Belt press feed pump-B | P-125B | 1 | MCC | S | 30 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 0 | 30 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
51 | Filterate Water Transfer Pump-A | P-127A | 1 | MCC | W | 9.3 | 7.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 9.3 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
51 | Filterate Water Transfer Pump-B | P-127B | 1 | MCC | S | 9.3 | 7.5 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 9.3 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
52 | Thickener overflow Water pump-A | P-124A | 1 | MCC | W | 45 | 37 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 45 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
52 | Thickener overflow Water pump-B | P-124B | 1 | MCC | S | 45 | 37 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 45 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
63 | Scale & Corrosion Inhibitor dosing pump-2 | P-213A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | … | DIRECT | OUTDOOR | 1 | 230 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC
63 | Scale & Corrosion Inhibitor dosing pump-2 | P-213B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | … | DIRECT | OUTDOOR | 1 | 230 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC
64 | Polymeric Dispersant dosing pump-A | P-214A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | … | DIRECT | OUTDOOR | 1 | 230 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC
64 | Polymeric Dispersant dosing pump-B | P-214B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | … | DIRECT | OUTDOOR | 1 | 230 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC
66 | Acid dosing pump-A | P-216A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.66 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
66 | Acid dosing pump-B | P-216B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.66 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
69 | Flocculator for Thickner | A-105 | 1 | MCC | W | 9.3 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.32 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 9.3 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
73 | Agitator for FeCl3 tank-A | A-105A | 1 | MCC | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
73 | Agitator for FeCl3 tank-B | A-105B | 1 | MCC | S | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
18 | PE dosing tank Agitator-A for HRSCC | A-106A | 1 | MCC | W | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.58 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
18 | PE dosing tank Agitator-B for HRSCC | A-106B | 1 | MCC | S | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.58 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 1.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
19 | Agitator for SMBS tank-A | A-107A | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.58 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
19 | Agitator for SMBS tank-B | A-107B | 1 | MCC | S | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 23.58 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
35 | Scale & Corrosion Inhibitor dosing tank-1 Agitator | A-109A | 1 | MCC | W | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.55 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
35 | Scale & Corrosion Inhibitor dosing tank-2 Agitator | A-109B | 1 | MCC | S | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.55 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 1.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
36 | Polymeric Dispersant dosing tank-1 Agitator | A-110A | 1 | MCC | W | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.37 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
36 | Polymeric Dispersant dosing tank-1 Agitator | A-110B | 1 | MCC | S | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.37 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 1.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
33 | Biocide-I dosing pump-A | P-208A | 1 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.3 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC | LOCAL VFD
33 | Biocide-I dosing pump-B | P-208B | 1 | MCC | S | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.3 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.37 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC | LOCAL VFD
22 | INDIRECT COOLING CIRCUIT |  |  | MCC | W |  |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.41 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
25 | Soft water supply pumps | PM-WTP-M-17-B | 1 | MCC | S | 200 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 2.23 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 200 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
37 | DIRECT COOLING SYSTEM & SLUDGE TREATMENT | FC-WTP-M-03-B |  | MCC | S |  |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 5.37 | V-BELT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
53 | Acid unloading pump | PM-WTP-M-13-A | 2 | MCC | W | 5.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 5.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
54 | PE unloading pump | PM-WTP-M-13-B | 2 | MCC | S | 5.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.011 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 5.5 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
56 | Scrapper mechanism in settler (Travel motion) |  | 1 | MCC | S | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
57 | Scrapper mechanism in settler (Hoisting motion) |  | 1 | MCC | W | 1.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | DOL-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
58 | Grab Bucket for scrapper | PM-WTP-M-20-B | 2 | MCC | S | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 3.7 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
59 | PE dosing pump-A for Belt press | P-211A | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
59 | PE dosing pump-A for Belt press | P-211B | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
60 | PE dosing pump-A for Longitudinal settling Tank | P-210A | 1 | MCC | S | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
60 | PE dosing pump-B for Longitudinal settling Tank | P-210B | 1 | MCC | S | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
61 | PE dosing pump-A for thickener | P-212A | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
61 | PE dosing pump-B for thickener | P-212B | 1 | MCC | W | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
| Biocide-1 Dosing Pump-2 for Filtered water cold welll | P-217A | 1
| Biocide-1 Dosing Pump-2 for Filtered water cold welll | P-217B | 1
| Biocide-2 Dosing Pump-2 for Filtered water cold welll | P-218A | 1
| Biocide-2 Dosing Pump-2 for Filtered water cold welll | P-218B | 1
62 | FeCl3 dosing pumps | PM-WTP-M-25-B | 2 | MCC | S | 0.75 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.004 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0 | 0.75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
65 | Hypo dosing pump | MK-WTP-M-01 | 2 | MCC | W | 0.37 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.66 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 0.37 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
67 | Oil skimmer-1 for settling tank | E-105 | 1 | MCC | W | 1.1 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.29 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 1.1 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
67 | Oil skimmer-2 for settling tank | E-105 | 1 | MCC | W | 1.1 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.29 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 1.1 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
68 | Mixer for BW sump | MK-WTP-M-04 | 4 | MCC | W | 9.3 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.29 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 9.3 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
70 | Mixer-A for Sludge storage tank | A-104A | 1 | MCC | W | 18.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.29 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 18.5 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
| Mixer-B for Sludge storage tank | A-104B | 1 | MCC | W | 18.5 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.29 | DIRECT | OUTDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 18.5 | 0
71 | Common DWPE tank mixer | LF-WTP-M-01 | 2 | MCC | W | 3.7 |  |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | LATER | DIRECT | OUTDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | VENDOR | MCC
73 | Agitator for FeCl3 tank-A | A-105A | 2 | MCC | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
73 | Agitator for FeCl3 tank-B | A-105B | 2 | MCC | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | DOL | NA | DOL-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
74 | Corrosion Inhibitor dosing tank mixer | PF | 1 | MCC | W | 1.5 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
75 | Antiscalant dosing tank mixer | PF | 1 | MCC | W | 1.5 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
76 | Flocculator -Belt press | PF | 2 | MCC | W | 2.2 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 2.2 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
77 | Thickener mechanism - Scrapper | PF | 1 | MCC | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
78 | Thickener - Lifting mechanism | PF | 1 | MCC | W | 1.5 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 1.5 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
79 | Machine | PF | 2 | MCC | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 1 | 230 | 50 | PF | NA | PF-2 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | MCC
80 | Air compressor |  | 1 |  | W | 30 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 30 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | 0
81 | For Belt filter press |  | 1 |  | W | 7.5 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 7.5 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | 0
82 | UV System |  | 1 |  | W | 3.7 |  |  | 1 |  | NA | NA | NA | NA | NA | NA | INDOOR | 3 | 415 | 50 | PF | NA | PF-1 | 3.7 | 0 |  |  | NO | NO | NO | NO | NO |  | NA |  | THERMAX-WWS | 0
41 | Scaled water from scale pit to Longitudinal settling tank Pump-A | P-120A | 1 | MCC | W | 250 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 250 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
41 | Scaled water from scale pit to Longitudinal settling tank Pump-B | P-120B | 1 | MCC | W | 250 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 250 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
41 | Scaled water from scale pit to Longitudinal settling tank Pump-C | P-120C | 1 | MCC | W | 250 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 250 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
41 | Scaled water from scale pit to Longitudinal settling tank Pump-D | P-120D | 1 | MCC | W | 250 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 250 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
41 | Scaled water from scale pit to Longitudinal settling tank Pump-E | P-120E | 1 | MCC | S | 250 | 250 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 1.5 | V-BELT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 0 | 250 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
43 | RHF exit and mill scale flume flushing pump-A | P-119A | 1 | MCC | W | 75 | 75 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.32 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 75 | 0 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
43 | RHF exit and mill scale flume flushing pump-B | P-119B | 1 | MCC | S | 75 | 75 |  | 1 |  | VENDOR TO FURNISH | VENDOR TO FURNISH | VENDOR TO FURNISH | LATER | 0.32 | DIRECT | OUTDOOR | 3 | 415 | 50 | VFD | NA | VFD-1 | 0 | 75 |  |  | NO | NO | NO | NO | NO |  | IP55 | IE3 | THERMAX-WWS | MCC
| Miscellaneous | [26 empty] | NO | NO | NO | NO | NO
| Cooling tower |  | 4 |  |  | 15 | [21 empty] | NO | NO | NO | NO | NO
| Pump houses |  | 3 |  |  | 5.5 | [21 empty] | NO | NO | NO | NO | NO
| Valves |  | 20 |  |  | 0.37 | [21 empty] | NO | NO | NO | NO | NO
| UPS |  | 1 |  |  | 20 | [21 empty] | NO | NO | NO | NO | NO
| NON UPS SUPPLY |  | 1 |  |  | 10 | [21 empty] | NO | NO | NO | NO | NO
| EOT CRANE |  | 1 |  |  | 5 | [21 empty] | NO | NO | NO | NO | NO
| WELDING RECP-63Amps |  | 2 |  |  | 35 | [21 empty] | NO | NO | NO | NO | NO
| LIGHTING FEEDER/PDB |  | 1 |  |  | 50 | [21 empty] | NO | NO | NO | NO | NO
sludge thickener hm-103 to add