## Busbar
| Bus bar Size for Panel |  |  | Sri Hanuman Bio Fuels Pvt ltd, 360, 361 & 362 of Arugolanu village, Bapulpadu Mandal, Krishna district, Andhra
Project Name : 300 KLPD AA Grain based Distillery on Broken Rice
Project Code : N-24022
| Bus bar Details |  |  | Bus bar Size Calculation
| Bus bar Current Details: |  |  | De rating Factors
| Rated Voltage (L-L): | 11 | Volt | Per Phase Bus Strip De rating Factor (K1) | 1 | 0.06
| Rated Frequency: | 50 | Hz | Busbar Insulating Material De rating Factor (K2) | 1
| Desire Maximum Current Rating : | 1236.15 | Amp | Busbar Position De rating Factor (K3) | 1
| Fault Current (Isc): | 50 | KA | Busbar Installation Media De rating Factor (K4) | 0.8
| Fault Duration (t): | 1 | Sec | Busbar Artificial Ventilation De rating Factor (K5) | 0.9
| Bus bar Temperature Details: |  |  | Enclosure & Ventilation De rating Factor (K6) | 0.95 | 0.004883%
| Operating Temperature of Bus bar (θ) | 45 | °c | Proxy Effect De rating Factor (K7) | 0.82 | 13
| Final Temperature of Bus bar during Fault(θ1) | 40 | °c | Altitude of Bus Bar installation De rating Factor (K8) | 0.84
| Temperature rise of Bus Bar Bar during Fault (θt=θ1-θ) | -5 | °c | Total Derating Factor: | 0.47114
| Ambient Temperature(θn): | 50 | °c | Busbar Size Calculation
| Maximum Bus Bar Temperature Rise: | -5 | °c | Desire Current Rating of Busbar (I2) | 1236.15 | Amp
| Enclosure Detail: |  |  | Current Rating of Busbar after Derating Factor (I1) | 2623.7469 | Amp
| Type of Panel | Cubical Type |  | Busbar Cross Section Area as per Current | 3279.6836 | Sq.mm
| Installation of Panel | Indoors (well Ventilated) |  | Busbar Cross Section Area as per Short Circuit | #NUM! | Sq.mm
| Altitude of Panel Installation on Site | 2900 | Meter | Final Calculated Bus Bar Cross Section Area | #NUM! | Sq.mm
| Panel Length | 800 | mm | Actual Cross Section Area of Busbar | 150 | Sq.mm
| Panel Width | 9600 | mm | #NUM!
| Panel Height | 2400 | mm | Forces generated on Bus Bar due to Short Circuit Current
| Panel Area: | 18432000000 | Sq.mm | Peak electro-magnetic forces between phase conductors (F1) | 363.3721 | Kg/cm2
| Bus bar Detail: |  |  | Peak electro-magnetic forces between phase conductors (F1) | 3.6337 | Kg/mm2
| Bus bar Material | Aluminium |  | Forces at the head of the Supports or Bus Bar (F) | 3.8154 | Kg/mm2
| Bus bar Shape | Flat Bars |  | Permissible Strength of Insulator (F') is | 10 | Kg/mm2
| Bus bar Strip Arrangements | Horizontal |  | Forces on Insulation is in within Limits
| Current Density of Bus Bar Material | 0.8 | A/Sq.mm | Mechanical strength of the busbars
| Temperature Co efficient of Material Resistance at 20°c(α20): | 0.00403 |  | Mechanical strength of the busbars | 90.8794 | Kg/cm2
| Material Constant(K): | 1.166 |  | Mechanical strength of the busbars | 0.90879 | Kg/mm2
12 | Bus bar Material Permissible Strength: | 1200 | Kg/cm2 | Permissible Busbar Strength is | 12 | Kg/mm2
| Bus bar Insulating Material: | Bare |  | Mechanical strength of Busbar is in within Limit
| Bus bar Position: | Edge-mounted bars |  | Temperature Rise Calculation
| Bus bar Installation Media: | Non-ventilated ducting |  | Specified Maximum Temperature Rise (T1) | -5 | °c
| Bus bar Artificial Ventilation Scheme: | without artificial ventilation |  | Calculated Maximum Temperature Rise (T2) | -1.4552 | °c
| Bus bar Size Detail: |  |  | Temperature Rise is high than define Limit
| Busbar Width(e): | 10 | mm
| Busbar Thickness(s): | 20 | mm | Results:
| Number of Bus Bar per Phase(n): | 30 | No's | Size of Busbar: 1 Nos X 30 X 5 Per Phase
| Total Busbar Area per Phase: | 150 | Sq.mm | Total No's of Busbar: 3 Nos X 30 X 5 for Phase and 1 Nos X 30 X 5 Per Neutral |  | 1
| Busbar Length per Phase(a): | 500 | mm | Forces at the head of the Supports or Bus Bar (F) :3.81540697674419Kg/mm2
| Distance between Two Bus Strip per Phase(e): | 30 | mm | Mechanical strength of the busbars :0.9Kg/mm2
| Busbar Phase Spacing (p): | 400 | mm | Maximum Temperature Rise :-1°c
| Total width of Bus bar per Phase(w): | 30 | mm
43 | Busbar Phase to Phase Distance (d): | 430 | mm
| Modulus of inertia of a busbar or of a set of busbars | 16.66 | cm3
| Total No of Circuit | 3
| Total Busbar Area for Enclosure | 900000 | Sq.mm
Busbar Support Insulator Detail:
50 | Distance between insulators on Same Phase(l): | 500 | mm
10 | Insulator Height (H) | 100 | mm
0.5 | Distance from the head of the insulator to the busbar centre of gravity (h): | 5 | mm
10 | Permissible Strength of Insulator (F'): | 1000 | Kg/cm2
Ref: Merlin Gerin design guide (IEC 60 694)
| Indoors (well Ventilated) |  | 2
Indoors (Poorly Ventilated)
Outdoor
Flat Bars
Round Bars
Hollow Round Bars
Bare
PVC Sleeving
Painted
Edge-mounted bars
1 bar base-mounted
several base-mounted bars
Calm indoor atmosphere
Calm outdoor atmosphere
Non-ventilated ducting
without artificial ventilation
with artificial ventilation
Horizontal
Vertical
Note on D29: Aluminum=0.8 Amp/Sq.mm Copper =1.6 Amp/Sq.mm
Note on D30: Aluminium=0.00403 Copper=0.00393
Note on D31: Aluminum=1.166 Copper=0.52
Note on D43: Normally Distance between each bar is equal to bus bar width

## Detating Factor
Various Derating Factor
Number of Bus bar Strip per Phase (K1) |  |  |  | Bus bar Insulating Material (K2): | De rating Factor
e/a | No of Bus bar per Phase |  |  | Bare | 1
| 1 | 2 | 3 | PVC Sleeving | 1.2
0.05 | 1 | 1.63 | 2.4 | Painted | 1.5
0.06 | 1 | 1.73 | 2.45 | Bus bar Position(K3): | De rating Factor
0.08 | 1 | 1.76 | 2.5 | Edge-mounted bars | 1
0.1 | 1 | 1.8 | 2.55 | 1 bar base-mounted | 0.95
0.12 | 1 | 1.83 | 2.6 | several base-mounted bars | 0.75
0.14 | 1 | 1.85 | 2.63 | Bus bar Installation Media(K4): | De rating Factor
0.16 | 1 | 1.87 | 2.65 | Calm indoor atmosphere | 1
0.18 | 1 | 1.89 | 2.68 | Calm outdoor atmosphere | 1.2
0.2 | 1 | 1.91 | 2.7 | Non-ventilated ducting | 0.8
Volume of Enclosure & Ventilation De rating Factor (K6) |  |  |  | Bus bar Artificial Ventilation Scheme (K5): | De rating Factor
cross Section area of Busbar/Total Bus bar Area | Indoors ( Panel is well Ventilated) | Indoors ( Panel is Poorly Ventilated) | Outdoor | without artificial ventilation | 0.9
0% | 0.95 | 0.85 | 0.65 | with artificial ventilation | 1
1% | 0.95 | 0.85 | 0.65 | Altitude of installation site (Meter) (K8) | De rating Factor
5% | 0.9 | 0.7 | 0.6 | 2200 | 0.88
10% | 0.85 | 0.65 | 0.5 | 2400 | 0.87
|  |  |  | 2500 | 0.86
|  |  |  | 2700 | 0.85
Value of Modulus of inertia of a bus bar or of a set of bus bars (i/v) |  |  | 1 | 2900 | 0.84
No of Bus Strip per Phase | Vertical Bus Bar (cm3) | Horizontal Bus Bar (cm3) | 3 | 3000 | 0.83
1 | 1.66 | 16.66 | 16.66 | 3300 | 0.82
2 | 14.45 | 33.33 |  | 3500 | 0.81
3 | 33 | 50 |  | 4000 | 0.78
|  |  |  | 4500 | 0.76
|  |  |  | 5000 | 0.74
|  |  |  | Proxiy Effect (K7): | De rating Factor
30 | 5 | 150 | 300 | 1 | 0.82
30 | 10 | 300 | 600 | 2 | 0.82
40 | 5 | 200 | 400 | 3 | 0.82
40 | 10 | 400 | 800 | 4 | 0.89
50 | 10 | 500 | 1000 | 5 | 0.95
60 | 10 | 600 | 1200 | 6 | 0.99
75 | 10 | 750 | 1500 | 7 | 1
80 | 10 | 800 | 1600
100 | 10 | 1000 | 2000